All Regional Engineers

Omer M. Osman, P.E.

Special Provision for Underpass Luminaire

April 18, 2014

This special provision was developed by the Bureau of Design and Environment to correct an inconsistency between the construction and material requirements for underpass luminaires and to require stainless steel vibration dampeners for suspended underpass luminaries.  It also allows aluminum luminaire housings as an alternative to stainless steel and it clarifies the material and construction requirements based on current installation and manufacturing procedures.

This special provision should be inserted in contracts requiring underpass luminaires.

The districts should include the BDE Check Sheet marked with the applicable special provisions for the August 1, 2014 and subsequent lettings.  The Project Development and Implementation Section will include a copy in the contract.

This special provision will be available on the transfer directory April 18, 2014.

80345m

# underpass luminaire (bde)

Effective:  August 1, 2014

Revise the first paragraph of Article 821.06 of the Standard Specifications to read:

“	821.06	Underpass Installation.  When attached directly to a structure, the underpass luminaire shall have stainless steel brackets installed between the luminaire and the structure to create a gap of not less than 1 in. (25 mm).”

Revise the third sentence of the third paragraph of Article 821.06 of the Standard Specifications to read:

“	All mounting hardware, including the vibration dampers, shall be stainless steel.”

Revise Article 1067.04(a) of the Standard Specifications to read:

“	(a)	Housing.  The housing and lens frame shall be made of heavy duty die cast aluminum or 16 gauge (1.5 mm) minimum thickness stainless steel according to ASTM A 269, Grade 304L.  All seams in the housing enclosure shall be welded by continuous welds.

The housing shall have an opening for installation of 3/4 in. (19 mm) diameter conduit.”

Revise the third sentence of the first paragraph of Article 1067.04(b) of the Standard Specifications to read:

“The lens frame shall be hinged with a continuous stainless steel piano type hinge for stainless steel housings.”

Revise the first sentence of the first paragraph of Article 1067.04(c) of the Standard Specifications to read:

“Four luminaire mounting brackets fabricated from 11 gauge (3.05 mm) stainless steel according to ASTM A 269, Grade 304L shall be used to attach the luminaire housing.”

80345