## TRAFFIC SIGNAL BATTERY BACKUP SYSTEM

GENERAL REQUIREMENTS: The Battery Back-up System (BBS) shall include, but not be limited to the following: inverter/charger, power transfer relay, batteries, battery cabinet, a separate failsafe automatic bypass switch and all necessary hardware and interconnect wiring. The BBS shall provide reliable emergency power to a traffic signal in the event of a power failure or interruption. The transfer from utility power to battery power and vice versa shall not interfere with the normal operation of traffic controller, conflict monitor/malfunction management unit or any other peripheral devices within the traffic controller assembly.

Additional information for the Uninterruptable Power Supply:

The UPS shall be capable of keeping the signals running green, yellow and red during periods of utility power failure. The UPS shall meet the following requirements:

1.	Maintain power for a minimum of 60 minutes upon power failure.

2.	Electrical inputs:

AC Input Voltage:……..	95-135 Volts

AC Input Current:……..	30 Amps Max

Frequency:…………….. Auto-sensing

3.	Electrical outputs:

AC Output Voltage: .........+/- 10% over input voltage range

Current:........................... 9.2A nominal

Power at 50°C:................1100W/VA

4. 	Display:

Full graphic LCD, 480x272 pixels, Resistive touch screen

5.    Dimensions:

Inches:............................5.22H x 15.5W x 8.75D

6.	A plug type connection (if possible) should output to the controller's "D" panel when the UPS battery is about to fail.

7. 	A heater shall be provided either internally or externally to maintain an adequate operation temperature for the UPS.  The batteries shall be kept charged by a balanced charging system.

8.	An automatic transfer switch shall be provided.

Basis of Payment: The above work will be paid for at the contract unit price Each for TRAFFIC SIGNAL BATTERY BACKUP SYSTEM shall be payment in full for all labor, materials, and equipment required to provide, install, and test the battery backup system described above, complete.